## NPSH
NPSHa | PSI | FEET
Atmospheric Available | 14.7 | 33.957 | Pool systems are considered 'open' systems default is 14.7 psi at sea leavel In a closed system this value is 0
Positive Suction Head | 0 | 0 | Enter in feet [0' if suction lift]
Suction Lift | 3.8095 | 8.8 | Enter gage reading, inches Hg: | 8
Hf of Suction Line | 0.8658 | 2 | Enter in feet [0' if suction gauge availabe]
Vapor Pressure | 0.51 | 1.1781 | Default value for 80°F pool water
| NPSHa | 21.9789
| Pump NPSHr | 15.6 | Take data from pump curve
| BUFFER NPSH | 6.3789 | NPSH buffer must be geater than NPSHr by 10% [min of 5']
| 110% of NPSHr: | 17.16
USER TO ENTER DATA INTO THE BLUE AREAS ONLY